IRQ2025-006

Annex (1.1): Bill of Quantities (BoQ) for Compact water unit – Capacity of 400 M3/hour

الوحدة المجمعــــة طاقة 400 م3/ ساعــة

| # | التفاصيل _ Description | Item Name | Origin | Brand Name |
| --- | --- | --- | --- | --- |
| 1 | تهيئة الموقع للوحدات المجمعة بأبعاد (12*30) م2 تجهيز المواد والمعدات اللازمة والقيام برفع كرفان بأبعاد (11*8.5) م وحاوية حديد والقيام بقشط الأرض الطبيعية بمقدار 40 سم مع نقل الأنقاض خارج موقع العمل والحدل الجيد بالمعدات الميكانيكية مع الرش وصولا الى درجة حدل 92% مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف. |  |  |  |
|  | Site preparation for the compact units (CUs) with dimensions of (12 × 30) m². Supply of all required materials and equipment and execution of lifting the caravan with dimensions of (11 × 8.5) m and the steel container. The work includes cutting the ground to a depth of 40 cm, removing debris outside the work site, and proper companion using mechanical equipment with water spraying to achieve a compaction degree of 92%, including all necessary works and as directed by the supervising engineer. |  |  |  |
| 2 | اعمــال الدفن: تجهيز المواد والمعدات اللازمة والعمل على دفن ارضية المجمع وصولا الى المنسوب المطلوب وباستخدام السبيس نوع B وعلى ان يكون الحدل على شكل طبقات مع الرش لكل طبقة بالماء على ان تكون نسبة الحدل 95 % مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف (طبقتان سمك 20 سم لكل طبقة). |  |  |  |
|  | Backfilling Works: Supply of all required materials and equipment, and execution of backfilling for the compound area up to the required level using sub-base type (B). The compaction shall be carried out in layers, with each layer properly watered and compacted to achieve a compaction degree of 95%. The work includes all necessary requirements and shall be carried out as directed by the supervising engineer (two layers, each 20 cm thick). |  |  |  |
| 3 | أعمال صب خرسانة القاعدة: - تجهيز المواد والمعدات اللازمة والقيام بصب خرسانة تعمية عادية غير مسلحة (Plain Concrete) مقاومة انضغاط (15) ميكا باسكال بإسمنت بورتلاندي مقاوم للأملاح بما في ذلك القوالب بسمك (10سم) تحت القاعدة الكونكريتية للوحدة المجمعة (حسب التصميم) شاملا" السعر فرش طبقة من النايلون تحت الخرسانة العادية. مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف. - تجهيز المواد والمعدات اللازمة والقيام بصب القاعدة الكونكريتية C35 بسمك 30 سم للوحدة المجمعة مع عمل قواعد كونكريتية لرفع الاحواض والفلاتر عن الارض باستعمال طبقتان من حديد التسليح قطر 16 ملم كل 15 بالاتجاهين مع عمل سواقي (حسب التصميم) مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف. |  |  |  |
|  | Base Concrete Works: - Supply of all required materials and equipment, and execution of plain, unreinforced concrete (Plain Concrete) with a compressive strength of 15 MPa using Portland cement resistant to salts, including formwork with a thickness of 10 cm beneath the concrete base of the prefabricated unit (as per design). This includes laying a layer of polyethylene (plastic) sheet under the plain concrete, along with all necessary works, as directed by the supervising engineer. - Supply of all required materials and equipment, and execution of the concrete base C35 with a thickness of 30 cm for the prefabricated unit, including construction of concrete pedestals to raise the tanks and filters above the ground. Reinforcement shall be provided using two layers of 16 mm diameter steel bars spaced at 15 cm in both directions, with construction of channels as per design. All works shall include necessary requirements and be carried out as directed by |  |  |  |
| 4 | الوحدة المجمعة: تصميم وتجهيز وتنفيذ ونصب وربط وفحص وتشغيل وحدة ماء مجمعة حسب المواصفات أدناه وبطاقة اجمالية 400 م3/ساعة Pressure Filter شاملا" السعر: - 1- تقديم مخططات تفصيلية لأعمال القاعدة الخرسانية للوحدة المجمعة (حجم A3، A4) ومصدق من قبل مديرية الماء قبل التنفيذ 2- تقديم مخططات تفصيلية لأعمال الميكانيكية والكهربائية وبنسختين (حجم A3، A4) 3- تقديم عرض فني متكامل لكافة اجزاء الوحدة ويتضمن العرض الفني كافة الكتلوكات للمواد المراد تجهيزها ضمن الوحدة المجمعة والابعاد والمخططات ID، Civil layout &P 4- تقديم برنامج الصيانة والتشغيل للوحدة المجمعة. 5- أذا كان تصنيع الأجزاء الحديدية للوحدة المجمعة (أحواض الترسيب، التخثير، أحواض التجميع، المرشحات) خارج العراق يجب أن تكون الشركة المصنعة حاصلة على شهادة الأيزو ولها خبرة لاتقل عن عشر سنوات في مجال قطاع المياه يحق للشركة المنفذة أن تقوم بتصنيع الأجزاء الحديدية الواردة أعلاه داخل العراق على أن تكون هذه الشركات حاصلة على موافقة وزارة االتخطيط وشهادةالأيزو سارية المفعول ولها خبرة لاتقل عن عشر سنوات في مجال قطاع المياه على أن يذكر ذلك في العرض الفني مع ذكر الدولة التي تم التصنيع فيها 6- يلتزم المقاول بتجهيز المعدات الميكانيكية والكهربائبة الداخلة في الوحدة المجمعة وفق المواصفات المرفقة طياً والتي تحتوي على تفاصيل أنواع المواد ومواصفاتها 7- ان يكون منشأ المضخات وتكون هذه المناشىء للمواد المجهزه من ماركات (Brands) المعتمدة لدى مديرية ماء البصرة ويتم استحصال موافقة مديرية ماء البصرة واللجان ذات العلاقة بالمديرية على الماركة المراد تجهيزها قبل المباشرة بأجراءات التجهيز ولاتعتبر موافقة دائرة المهندس المقيم موافقه نهائية لاختيار اي ماركة من المواد المجهزة مالم يتم امال الاجراءات المشار اليها اعلاه 8- ان يكون منشأ (اجهزة الكلورين مع البوسترات، خلاط الشب وخلاط المزج البطيء، الصمامات، ضاغطات الهواء، قواطع الدورة والمشغلات الكهربائية) من المناشئ المعتمدة لدى مديرية مـــاء البصرة. 9- القابلوات من المناشىء للمواد المجهزة من ماركات (Brands) المعتمدة لدى مديرية ماء البصرة ويتم استحصال موافقة مديرية ماء البصرة واللجان ذات العلاقة بالمديرية على الماركة المراد تجهيزها قبل المباشرة بأجراءات التجهيز ولاتعتبر موافقة دائرة المهندس المقيم موافقه نهائية لاختيار اي ماركة من المواد المجهزة مالم يتم امال الاجراءات المشار اليها اعلاه 10- فحص الطرف الثالث يجب ان يتضمن: - - فحص سمك البليت للأحواض والفلاتر وسمك بليت النوزلات - فحص الصبغ من الداخل والخارج وفحص سمية مادة الطلاء الداخلي - قياس الأبعاد للأجزاء الحديدية - فحص اللحام باليزر - فحص سمك الأنابيب وسمك الغلونة ونوع الفلنجات المستخدمة - فحص المضخات ويشمل فحص (مادة البدي والبشارة والشفت) وفحص البلورات والكمبريسر والأقفال ولوحة السيطرة ومطابقتها بالمواصفات المطلوبة - فحص الخلاطات والبوسترات والحاقنات لأجهزة الكلورين ومطابقتها بالمواصفات المطلوبة ويكون تقرير الفحص معزز بالصور والأرقام التسلسلية للأجزاء المفحوصة وكذلك نتائج الفحوصات التي تم القيام بها لأجزاء الوحدة الوحدة المجمعة والرمل والحصى يجب ان يكون ناجح بالفحص الكيميائي والفيزيائي 11- يجب ان تكون العكارة للماء المنتج اقل من 5Ntu 12- خزانات الشب والأنابيب البلاستيكية وملحقاتها يجب ان تكون مطابقة للمواصفات المطلوبة ويكون منشـــا المواد من المناشئ المعتمدة لدى مديرية مـــاء البصرة. 13- على الشركة المنفذة صيانة وتشغيل كافة فقرات الوحدة المجمعة وملحقاتها ولمدة سنة كاملة ويكون كادر التشغيل والصيانة مكون من (فني كهرباء، فني ميكانيك، مشغلين عدد/4) 14- تقديم شهادة منشأ للمعدات الميكانيكية والكهربائية الداخلة في الوحدة المجمعة |  |  |  |
|  | Compact Water Unit: Design, supply, fabrication, installation, connection, testing, and commissioning of a compact water treatment unit with a total capacity of 400 m³/hour (Pressure Filter type), including all related costs, as per the following specifications: - Submission of detailed drawings for the concrete foundation works of the compact unit (A3 and A4 sizes), duly approved by the Directorate of Water before implementation. - Submission of detailed mechanical and electrical drawings in two copies (A3 and A4 sizes). - Submission of a comprehensive technical offer covering all parts of the unit. The technical offer shall include complete catalogues for all materials and equipment to be supplied within the compact unit, in addition to detailed dimensions and drawings (ID, Civil Layout, and P&ID). - Submission of a maintenance and operation program for the compact unit. - If the fabrication of steel components of the compact unit (sedimentation tanks, coagulation tanks, collection tanks, filters) is carried out outside Iraq, the manufacturing company must hold an ISO certificate and have not less than 10 years of experience in the water sector. - The executing company may fabricate the above-mentioned steel parts inside Iraq, provided that these companies have approval from the Ministry of Planning, hold a valid ISO certificate, and have not less than 10 years of experience in the water sector. - This information shall be clearly stated in the technical offer, along with the country of manufacture. - The contractor shall supply all mechanical and electrical equipment for the compact unit according to the attached specifications, which include full details of material types and characteristics. - The pumps and all supplied materials shall be from brands approved by the Basra Water Directorate. Approval from the Basra Water Directorate and the relevant committees must be obtained for the selected brand prior to the commencement of procurement procedures. The approval of the Resident Engineer shall not be considered final until all the above-mentioned approvals are obtained. - The chlorination equipment (including boosters), rapid and slow mixers, valves, air compressors, circuit breakers, and electrical actuators shall be from approved sources recognized by the Basra Water Directorate. - All cables shall also be from approved brands accepted by the Basra Water Directorate. Official approval from the Directorate and relevant committees must be obtained before procurement, and the Resident Engineer’s approval shall not be considered final without completion of these procedures. - Third-party inspection shall include the following: - Measurement of plate thickness for tanks, filters, and nozzle plates. - Inspection of painting (internal and external) and testing the toxicity of the internal coating. - Measurement of dimensions of the steel components. - Laser testing of welds. - Inspection of pipe thickness, galvanization thickness, and type of flanges used. - Testing of pumps, including inspection of the body material, impeller, and shaft; testing of bearings, compressor, seals, and control panel for compliance with required specifications. - Testing of mixers, boosters, and chlorine injectors to ensure conformity with required specifications. - The inspection report must include photos, serial numbers of inspected components, and test results of the compact unit parts. - The sand and gravel used shall successfully pass chemical and physical tests. - The turbidity of the treated water shall be less than 5 NTU. - The alum tanks, plastic pipes, and their accessories shall conform to the required specifications, and the origin of materials shall be from approved sources recognized by the Basra Water Directorate. - The executing company shall be responsible for the operation and maintenance of all components and accessories of the compact unit for one full year. - The operation and maintenance team shall consist of: one electrical technician, one mechanical technician, and four operators. - The contractor shall provide a Certificate of Origin for all mechanical and electrical equipment included in the compact unit. Would you like me to make this translation formatted for inclusion in a tender document (e.g., numbered, with consistent technical language and indentation)? It would make it look more professional for submission. |  |  |  |
| 5 | لوحة التوزيع الرئيسية: تجهيز المواد والمعدات اللازمة لأعمال تجهيز المواد المدرجة أدناه والخاصة بلوحة التوزيع الرئيسية للوحدة المجمعة وتشمل: - تجهيز ونصب قاطع دورة ثلاثي الأطوار فرعي سعة 630 امبير عدد/ 1 - تجهيز ونصب قاطع دورة ثلاثي الأطوار فرعي سعة 100 امبير عدد/ 1 ويشمل العمل تجهيز ومد وربط قابلو مسلح مصنوع من النحاس قياس (4×120) ملم2 يمتد من لوحة التوزيع الرئيسية الى لوحة تشغيل الوحدة المجمعة يمد على تري كيبل حديد عرض 5 سم مع كل مايتطلبه العمل من مواد وحسب توجيهات المهندس المشرف ملاحظة: - تكون جميع القابلوات وقواطع الدورة خاضعة للفحص وناجحة. |  |  |  |
|  | Main Distribution Panel: Supply of all required materials and equipment for the works related to the main distribution panel of the compact unit, including: - Supply and installation of one (1) three-phase circuit breaker with a capacity of 630 A (sub-main). - Supply and installation of one (1) three-phase circuit breaker with a capacity of 100 A (sub-main). The work includes supplying, laying, and connecting an armored copper cable (4×120 mm²) extending from the main distribution panel to the control panel of the compact unit. The cable shall be laid on a steel cable tray with a width of 5 cm, including all materials and accessories required to complete the work, and in accordance with the supervising engineer’s instructions. Note: All cables and circuit breakers shall be tested and approved prior to use. |  |  |  |
| 6 | مضخات السحب الواطيء: تجهيز المواد والمعدات اللازمة والقيام بتجهيز ونصب وتشغيل مضخات افقية متكاملة من (المضخة+المحرك الكهربائي + المشغل الكهربائي نوع Star-Delta) طاقة 500 م3/س وضغط 25م مطابقة للمواصفات وتكون المناشئ للمواد المجهزة من ماركات ( Brands ) المعتمدة لدى مديرية ماء البصرة ويتم استحصال موافقة مديرية ماء البصرة واللجان ذات العلاقة بالمديرية على الماركة المراد تجهيزها قبل المباشرة بإجراءات التجهيز ولا تعتبر موافقة دائرة المهندس المقيم موافقة نهائية لاختيار أي ماركة من المواد المجهزة ما لم يتم أكامل الاجراءات المشار أليها أعلاه و تنصب داخل حوض من الكونكريت المسلح داخل المشروع وكما يلي :- - تجهيز كافة المواد والملحقات الخاصة بالربط (كافة الملحقات والانابيب التي تستخدم في جهتي السحب والدفع للمضخات تكون من حديد الكاربون ستيل سمك لا يقل عن 8 ملم) مع تجهيز ونصب كافة الملحقات اللازمة للربط من عكوس وتقاسيم ومصغرات مع اعمال القطع واللحام كما يشمل العمل تجهيز الاقفال جميعها تكون من نوع فراشة كيربوكس دبل فلنج ومانع أهتزاز واقفال مانعة الرجوع دبل فلنج على جهة الدفع وممص عل جهة السحب للمضخة وحسب توجيهات المهندس المشرف - يكون قياس كافة الملحقات جهتي السحب والدفع أكبر من فلنجة السحب والدفع (100ملم) - تجهيز ونصب هيدر 400 ملم كاربون ستيل يربط على المضخات من جهة وعلى انبوب الذاهب للوحدة المجمعة من جهة اخرى - نصب المضخة مع عمل قاعدة حديدية جديدة ورفع المضخة القديمة واستبدال الشيلمان التالف مع وضع مشبكات جديدة للارضية - تجهيز ومد وربط كافة القبلوات الملائمة بين الى لوحة توزيع محطة السحب الواطيء الجديدة الى الستارتر ومن الستارتر الى المضخة يوضع داخل تري حديد ... مع كل ما يتطلبه العمل وحسب توجيهات المهندس المشرف. مواصفات المضخات: النوع: Double section pump RPM: 1500 دورة بالدقيقة نوع البشارة: - S – bronze الشفت: ستنلس ستيل SS- 420 Soft packing PUMPLUPRICATION= (single point automatic lubricator) Npsh-Required<=4m Pump case outside coating = powder coating Pump case in side coating = epoxy coating Pump case (ductile iron or cast iron) نوع المشغل للمضخة: محرك كهربائي فولتية المحرك: 380 فولت قدرة المحرك تغطي نهاية منحنى أداء المضخة التردد: 50 هيرتز سرعة دوران المحرك: 1000-1500 دورة بالدقيقة صنف العزل: F نوع الحماية: 55IP- درجة حرارة المحيط: 55 درجة سيليزية مع كل ما يتطلبه العمل وحسب توجيهات المهندس المشرف. |  |  |  |
|  | Low Lift Pumps: Supply of all required materials and equipment, and execution of the supply, installation, and commissioning of horizontal centrifugal pumps, complete with pump + electric motor + electrical starter (Star-Delta type), with a capacity of 500 m³/hr and head of 25 m, fully compliant with the specifications. All supplied materials shall be from brands approved by the Basra Water Directorate, and official approval from the Directorate and the relevant committees must be obtained for the selected brand prior to commencing procurement procedures. The approval of the Resident Engineer shall not be considered final until all required approvals are completed as stated above. The pumps shall be installed inside a reinforced concrete sump within the project, as detailed below: - Supply of all connection materials and accessories: - All fittings and pipes used on both suction and discharge sides shall be carbon steel with a minimum thickness of 8 mm. - The work includes the supply and installation of all necessary fittings such as reducers, tees, elbows, and other accessories, including cutting and welding works. - The work also includes supplying all valves as follows: - Butterfly valves with gearbox, double flange type. - Anti-vibration joints. - Non-return valves (double flange type) on the discharge side. - Foot valves on the suction side. - All work shall be carried out according to the supervising engineer’s instructions. - All accessories on both suction and discharge sides shall have a diameter larger than the suction and discharge flanges by 100 mm. - Supply and installation of a 400 mm carbon steel header, connected to the pumps on one side and to the pipeline leading to the compact unit on the other. - Installation of the pump with fabrication of a new steel base, removal of the existing pump, replacement of any damaged steel channels, and installation of new floor gratings. - Supply, laying, and connection of all suitable electrical cables from the new low lift station distribution panel to the starter, and from the starter to the pump, placed inside a steel cable tray, including all necessary materials and works, as directed by the supervising engineer. Pump Technical Specifications: - Type: Double section pump - Speed (RPM): 1500 rpm - Impeller material: S–Bronze - Shaft material: Stainless steel (SS–420) - Sealing type: Soft packing - Pump lubrication: Single-point automatic lubricator - NPSH required: ≤ 4 m - Pump casing: - External coating: Powder coating - Internal coating: Epoxy coating - Material: Ductile iron or cast iron - Pump driver: Electric motor - Motor voltage: 380 V - Motor capacity: Suitable to cover the end point of the pump performance curve - Frequency: 50 Hz - Motor speed: 1000–1500 rpm - Insulation class: F - Protection class: IP55 - Ambient temperature: 55°C Including all necessary works, accessories, testing, and commissioning, and in accordance with the supervising engineer’s instructions. |  |  |  |
| 7 | لوحة السيطرة لمحطة السحب الواطئ: تجهيز المواد والمعدات اللازمة لأعمال تجهيز المواد المدرجة أدناه والخاصة بوحدات السيطرة الرئيسية لمحطة السحب الواطئ مواد وتكون جميع المواد خاضعة لفحص دائرة الكهرباء وتشمل: تجهيز وربط لوحة سيطرة رئيسية كاملة وباستخدام حديد سمك 2ملم مع البازبارات نحاسية ومقاييس التيار والفولتية والسلكترات ومصابيح ومفاتيح التشغيل مع تجهيز قواطع الدورة أدناه: - - تجهيز ونصب قاطع دورة ثلاثي الأطوار رئيسي سعة 250امبير عدد/1. - تجهيز ونصب قاطع دورة فرعي ثلاثي الأطوار سعة 160 أمبير عدد/2 - تجهيز ونصب قاطع دورة فرعي ثلاثي الأطوار سعة 63 أمبير عدد/2 مع كل ما يتطلبه العمل من مواد وحسب توجيهات المهندس المشرف يكون منشأ القواطع من المناشئ المعتمدة لدى مديرية مــاء البصــرة ويكون منشأ القابلوات من المناشئ المعتمدة لدى مديرية مــاء البصــرة وتكون هذه المناشئ للمواد المجهزة من ماركات (Brands) المعتمدة لدى مديرية ماء البصرة ويتم استحصال موافقة مديرية ماء البصرة واللجان ذات العلاقة بالمديرية على الماركة المراد تجهيزها قبل المباشرة بأجراءات التجهيز ولا تعتبر موافقة دائرة المهندس المقيم موافقة نهائية لأختيار أي ماركة من المواد المجهزة ما لم يتم أكمال الاجراءات المشار أليها أعلاه وحسب المواصفات الكهربائية المعتمدة لدى مديرية توزيع كهرباء البصرة - يجب ان يكون IP للوحة هو 54 - أبعاد اللوحة لا تقل عن (120×100×40) سم ملاحظة: - تكون جميع القابلوات وقواطع الدورة خاضعة للفحص وناجحة. |  |  |  |
|  | Control Panel for Low Lift Station: Supply of all required materials and equipment for the works related to the main control units of the low lift station, including all materials subject to inspection and approval by the Electricity Directorate. The works include supplying and connecting a complete main control panel, fabricated from 2 mm thick steel sheet, equipped with copper busbars, ammeter, voltmeter, selector switches, indicator lamps, and control switches, in addition to supplying and installing the following circuit breakers: a. Supply and installation of one (1) main three-phase circuit breaker with a capacity of 250 A. b. Supply and installation of two (2) sub three-phase circuit breakers with a capacity of 160 A each. c. Supply and installation of two (2) sub three-phase circuit breakers with a capacity of 63 A each. All required materials and works shall be provided in accordance with the supervising engineer’s instructions. - The circuit breakers shall be from brands approved by the Basra Water Directorate. - The cables shall also be from brands approved by the Basra Water Directorate. - All supplied materials shall be from approved brands (Brands) recognized by the Basra Water Directorate, and official approval must be obtained from the Directorate and its relevant committees for the selected brand prior to the commencement of procurement procedures. - The approval of the Resident Engineer shall not be considered final for the selection of any brand unless all the above procedures are completed, and all specifications shall comply with the electrical standards approved by the Basra Electricity Distribution Directorate. Additional requirements: - The protection degree (IP) of the panel shall be IP54. - The panel dimensions shall not be less than (120 × 100 × 40) cm. Note: All cables and circuit breakers shall be tested and approved prior to use. |  |  |  |
| 8 | أنبوب السحب الواطئ: تجهيز المواد والمعدات الازمة والعمل تجهيز ومد وربط وفحص انبوب دكتايل كبس قطر 400 ملم من يكون كأنبوب سحب يمتد على طول هيكل السحب وصولا" الى احواض الترسيب في موقع الوحدة المجمعة (ISO2531 FOR PIPE) (ISO4179 FOR CEMENT MORTER LINING) (ISO8179 FOR METAL ZINC COTING) ISO 4633 FOR EPDM Rubber GASKAT)) ويشمل العمل ربط وتثبيت الانبوب بواسطة اجنحة على ممشى هيكل السحب بأطواق حديدية مع عمل قواعد كونكريتية على الارض الترابية لمــد الانبوب مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف. |  |  |  |
|  | Low Lift Suction Pipe: Supply of all required materials and equipment, and execution of works for the supply, laying, connection, and testing of a ductile iron (DI) pipe, 400 mm diameter, to serve as the suction pipeline extending along the suction structure up to the sedimentation tanks at the compact unit site. The pipe and its components shall comply with the following standards: - ISO 2531 – for ductile iron pipes - ISO 4179 – for cement mortar lining - ISO 8179 – for metallic zinc coating - ISO 4633 – for EPDM rubber gaskets The work includes installation and fixing of the pipe along the suction structure walkway using steel clamps and supports, as well as construction of concrete bases on the ground to support the pipeline, including all necessary works and materials, and in accordance with the supervising engineer’s instructions. |  |  |  |
| 9 | عمل سقيفه key-span للوحدة المجمعة: تجهيز المواد والمعدات اللازمة والقيام بأنشاء سقيفه (key span) بأبعاد (30×12) م سمك 0.7 ملم فوق المجمع على ان تقسم الى مقطعين ( خانتين ) (تكون الاعمدة باستخدام حديد شيلمان I-section قياس 8" ويحيط بأعلى السقيفة شيلمان قياس 6" والساقية سمك لايقل عن 4 ملم مع استخدام مقصات بين عمود واخر باستخدام مقاطع زاوية قياس 3" ) شاملا العمل كافة اعمال الهيكل الحديدي والسقف و الكونكريت المسلح للأسس وبنسبة خلط (3:1,5:1) باستخدام السمنت المقاوم للأملاح وعلى المقاول تقديم كافة التفاصيل المعمارية والإنشائية للمهندس المشرف لاستحصال الموافقة كما ويشمل السعر تجهيز وتركيب واعمال الإنارة والكهربائيات ويشمل العمل طلاء كافة الاجزاء الحديدية للسقيفة بطبقتين من مانع الصدأ وثلاث طبقات من طلاء البوية باللون الذي يتفق عليه مع المهندس المشرف مع تجهيز ونصب بروجكتر LED ( 200واط ) عدد / 10 مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف. - منشأ الحديد من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - منشأ الاسمنت من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - منشأ الإنارة من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - منشأ الأسلاك من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - يكون أدنى ارتفاع للسقيفة اعلى من الاحواض بما لايقل عن 2م الذرعة الواردة في حقل الكميات تشمل ذرعة كلية لسقيفتين تنفذ كل سقيفة منها بشكل منفصل عن السقيفة الاخرى وبموجب المواصفات المذكورة اعلاه لكل سقيفة من السقائف |  |  |  |
|  | Construction of Key-Span Roof for the Compact Unit: Supply of all required materials and equipment, and execution of works to construct a Key-Span type roof with dimensions of (30 × 12) m and a sheet thickness of 0.7 mm above the compact unit. The roof shall be divided into two sections (bays). - The columns shall be fabricated using I-section steel (8"), and the top perimeter beam shall be made of I-section steel (6"). - The gutters shall have a thickness of not less than 4 mm. - Bracings between columns shall be made of angle sections (3"). - The works include fabrication and erection of the entire steel structure, roofing system, and reinforced concrete foundations with a concrete mix ratio of (1:1.5:3) using sulfate-resistant cement. - The contractor shall submit all architectural and structural details to the supervising engineer for approval prior to execution. The scope of work also includes: - Supply, installation, and connection of lighting and electrical systems. - Painting of all steel parts with two coats of anti-rust primer and three coats of finish paint in a color approved by the supervising engineer. - Supply and installation of ten (10) LED projectors, 200 W each. All works shall include all requirements and be executed as directed by the supervising engineer. Material origins: - Steel shall be from sources approved by the Basra Water Directorate. - Cement shall be from sources approved by the Basra Water Directorate. - Lighting fixtures shall be from sources approved by the Basra Water Directorate. - Electrical wires shall be from sources approved by the Basra Water Directorate. Additional requirements: - The minimum height of the roof shall be at least 2 m above the top of the tanks. - The quantity stated in the Bill of Quantities (BOQ) represents the total quantity for two separate roofs, each to be constructed independently in accordance with the above specifications. |  |  |  |

Datasheet, specification, photos of the items to be shared with the technical offer

Delivery Period in days: ___________________

Name of Contractor:______________________

Date:___________________________________

Stamp:_________________________________

Signature:___________________________