IRQ2025-006

Annex (2.1): Bill of Quantities (BoQ) for Compact water unit – Capacity of 200 M3/hour

الوحدة المجمعــــة طاقة 200 م3/ ساعــة

| # | التفاصيل _ Description | Item Name | Origin | Brand Name |
| --- | --- | --- | --- | --- |
| 1 | تفكيك ونقل الوحدة المجمعة القديمة تجهيز المواد والمعدات اللازمة والقيام بتفكيك كافة اجزاء الوحدة المجمعة طاقة 200 م3 / س تفكيك نظامي مع الحفاظ على جميع الاجزاء من التلف ونقلها الى مخازن المديرية مع فتح السقيفة واعادة نصبها بعد انتهاء العمل إذا تطلب العمل ذلك مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف. |  |  |  |
|  | Dismantling and Relocation of the Old Compact Unit Prepare the necessary materials and equipment and carry out the systematic dismantling of all components of the compact unit with a capacity of 200 m³/h, ensuring that all parts are preserved from damage. Transport the dismantled components to the Directorate’s storage. If required, open the shed and reinstall it after completion of the work, along with all other work requirements, in accordance with the instructions of the supervising engineer. |  |  |  |
| 2 | أعمال صب خرسانة القاعدة: تجهيز المواد والمعدات اللازمة والقيام بصب القاعدة الكونكريتية C35 بسمك 30 سم للوحدة المجمعة مع عمل قواعد كونكريتية لرفع الاحواض والفلاتر عن الارض باستعمال طبقتان من حديد التسليح قطر 16 ملم كل 15 بالاتجاهين مع عمل سواقي (حسب التصميم ) مع كافة متطلبات العمل وحسب توجيهات المهندس المشرف .. |  |  |  |
|  | Concrete Base Works: Prepare the necessary materials and equipment and carry out the casting of the C35 concrete base with a thickness of 30 cm for the compact unit, including the construction of concrete foundations to elevate the tanks and filters from the ground. Use two layers of reinforcement bars with a diameter of 16 mm, spaced every 15 cm in both directions, and construct channels as per the design. All work shall be performed in accordance with the work requirements and under the supervision and instructions of the supervising engineer. |  |  |  |
| 3 | الوحدة المجمعة: تصميم وتجهيز وتنفيذ ونصب وربط وفحص وتشغيل وحدة ماء مجمعة حسب المواصفات أدناه وبطاقة اجمالية 200 م3/ساعة Pressure Filter شاملا" السعر: - - تقديم مخططات تفصيلية لأعمال القاعدة الخرسانية للوحدة المجمعة (حجم A3، A4) ومصدق من قبل مديرية الماء قبل التنفيذ - تقديم مخططات تفصيلية لاعمال الميكانيكية والكهربائية وبنسختين (حجم A3، A4) - تقديم عرض فني متكامل لكافة اجزاء الوحدة ويتضمن العرض الفني كافة الكتلوكات للمواد المراد تجهيزها ضمن الوحدة المجمعة والابعاد والمخططات ID , Civil layout &P - تقديم برنامج الصيانة والتشغيل للوحدة المجمعة. - أذا كان تصنيع الأجزاء الحديدية للوحدة المجمعة (أحواض الترسيب، التخثير، أحواض التجميع، المرشحات،) خارج العراق يجب أن تكون الشركة المصنعة حاصلة على شهادة الأيزو ولها خبرة لاتقل عن عشر سنوات في مجال قطاع المياه يحق للشركة المنفذة أن تقوم بتصنيع الأجزاء الحديدية للوحدة أعلاه داخل العراق على أن تكون هذه الشركات حاصلة على موافقة وزارة التخطيط وشهادة الأيزو سارية المفعول ولها خبرة لاتقل عن عشر سنوات في مجال قطاع المياه على أن يذكر ذلك في العرض الفني مع ذكر الدولة التي تم التصنيع فيها - يلتزم المقاول بتجهيز المعدات الميكانيكية والكهربائبة الداخلة في الوحدة المجمعة وفق المواصفات المرفقة طياً والتي تحتوي على تفاصيل أنواع المواد ومواصفاتها - ان يكون منشأ المضخات ويكون منشـــا المواد من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - ان يكون منشأ (اجهزة الكلورين مع البوسترات، خلاط الشب وخلاط المزج البطيء ,الصمامات , ضاغطات الهواء، قواطع الدورة والمشغلات الكهربائية) ويكون منشـــا المواد من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - القابلوات ويكون منشـــا المواد من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - فحص الطرف الثالث يجب ان يتضمن: - - فحص سمك البليت للأحواض والفلاتر وسمك بليت النوزلات - فحص الصبغ من الداخل والخارج وفحص سمية مادة الطلاء الداخلي - قياس الأبعاد للأجزاء الحديدية - فحص اللحام باليزر - فحص سمك الأنابيب وسمك الغلونة ونوع الفلنجات المستخدمة - فحص المضخات ويشمل فحص (مادة البدي والبشارة والشفت) وفحص البلورات والكمبريسر والأقفال ولوحة السيطرة ومطابقتها بالمواصفات المطلوبة - فحص الخلاطات والبوسترات والحاقنات لأجهزة الكلورين ومطابقتها بالمواصفات المطلوبة - ويكون تقرير الفحص معزز بالصور والأرفام التسلسلية للأجزاء المفحوصة وكذلك نتائج الفحوصات التي تم القيام بها لأجزاء الوحدة الوحدة المجمعة. - الرمل والحصى يجب ان يكون ناجح بالفحص الكيميائي والفيزيائي - يجب ان تكون العكارة للماء المنتج اقل من 5Ntu - خزانات الشب والأنابيب البلاستيكية وملحقاتها يجب ان تكون مطابقة للمواصفات المطلوبة ويكون منشـــا المواد من المناشئ المعتمدة لدى مديرية مـــاء البصرة. - على الشركة المنفذة صيانة وتشغيل كافة فقرات الوحدة المجمعة وملحقاتها ولمدة سنة كاملة ويكون كادر التشغيل والصيانة مكون من (فني كهرباء، فني ميكانيك، مشغلين عدد/4) - تقديم شهادة منشأ للمعدات الميكانيكية والكهربائية الداخلة في الوحدة المجمعة. |  |  |  |
|  | Compact Unit: Design, supply, manufacture, installation, connection, testing, and operation of a compact water unit in accordance with the specifications below, with a total capacity of 200 m³/h for Pressure Filter, including the price: - Submission of detailed drawings for the concrete base works of the compact unit (sizes A3 and A4), approved by the Water Directorate prior to execution. - Submission of detailed mechanical and electrical drawings in two copies (sizes A3 and A4). - Submission of a comprehensive technical proposal covering all parts of the unit, including technical specifications of all materials to be supplied, dimensions, and drawings (ID, Civil Layout & P). - Submission of the maintenance and operation program for the compact unit. - If the fabrication of the steel components of the unit (sedimentation tanks, flocculation tanks, collection tanks, filters, etc.) is outside Iraq, the manufacturer must hold a valid ISO certification and have a minimum of ten years of experience in the water sector. - The executing company may manufacture the above steel components within Iraq, provided the company has approval from the Ministry of Planning, holds a valid ISO certificate, and has at least ten years of experience in the water sector. This must be indicated in the technical proposal, specifying the country of manufacture. - The contractor shall supply the mechanical and electrical equipment included in the compact unit according to the attached specifications, which detail the types of materials and their specifications. - Pumps and materials must originate from manufacturers approved by the Basra Water Directorate. - Equipment such as chlorine devices with boosters, slow mixers, valves, air compressors, circuit breakers, and electrical actuators must originate from manufacturers approved by the Basra Water Directorate. - Cables and associated materials must originate from manufacturers approved by the Basra Water Directorate. - Third-party inspection shall include: - Measurement of plate thickness for tanks and filters, and nozzle plate thickness. - Inspection of internal and external coating and testing of the coating material’s toxicity. - Dimensional verification of steel components. - Laser welding inspection. - Measurement of pipe thickness, coating thickness, and verification of flange types used. - Inspection of pumps, including inspection of body, impeller, and shaft; testing of bearings, compressors, locks, and control panels to ensure compliance with specifications. - Inspection of mixers, boosters, and chlorine injectors to ensure compliance with specifications. - Inspection reports shall include photographs, serial numbers of inspected parts, and results of all performed tests. - Sand and gravel must pass chemical and physical testing. - The produced water turbidity must be less than 5 NTU. - Screens, plastic pipes, and associated accessories must comply with required specifications and originate from manufacturers approved by the Basra Water Directorate. - The executing company shall operate and maintain all components of the compact unit and its accessories for one full year. The operation and maintenance team shall consist of 1 Electrical Technician, 1 Mechanical Technician, and 4 Operators. - Submission of Certificates of Origin for all mechanical and electrical equipment included in the compact unit. |  |  |  |

Datasheet, specification, photos of the items to be shared with the technical offer

Delivery Period in days: ___________________

Name of Contractor:______________________

Date:___________________________________

Stamp:_________________________________

Signature:___________________________