## WatHab Estimation
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
RO UNIT - 4 M3/hr / TDS UP TO 3,000 PPM ,
Supply and Installation for Reverse Osmosis Plant with production capacity of 4 M3/hr تجهيز ونصب محطة تحلية مياه بطاقة انتاجية 4 متر مكعب بالساعة تعمل على املاح لغاية 3,000
Babel Governorate /Al-Musayab District /Abu Jassim Village محافظة بابل/ قضاء المسيب / قرية أبو جاسم
Item |  | Description | Unit | Qty | Unit Pric( IQD) |  | Total Unit Price
[5 empty] | Provision | Installation | (IQD)
1 | اعمال ربط مصدر الماء الخام | Connection to Water Source
1.1 | مضخة الخاصة بتجهيز المياه عن طريق البئر المواصفات مدرجة في فقرة 1.1 | Raw Water Pump (Connection via shallow well ) See Specification 1.1 | Nos | 1
1.2 | مضخة الماء الخام المواصفات مدرجة في فقرة 1.2 | Raw Water Pump ( Connection via water network system) See Specification 1.2 | Nos | 1
1.3 | اعمال ربط الانابيب وخط مصدر الطاقة للمضخة الماء الخام المواصفات مدرجة في فقرة 1.3 | Extend for the Pipline & Electrical Conduit from the shallow well to the Raw water Tank See Specification 1.3 | LS | 1
2 | تجهيز ونصب محطة التحلية سعة 2 متر مكعب بالساعة | Supply and Installation for Reverse Osmosis Plant with production capacity of 4 M3/hr :
Supplying and Installation for brackish Water Desalination Plant with a production capacity of 4 cubic meters/hour . The RO unit consist of pretreatment units , RO unit modules , post treatment , instruments and control cabinant system. The main RO units should be assembled on a stainless Steel skid ( Resistant to Salinity ) to be be installed inside caravan and according to the instructions of supervisor engineer. ,All the details are listed under the Technical Specification . The works inludes also provision of labors, materials, and tools for installation , commissioning and testing for pump, the proper connection between tanks ( raws & product water tanks) and RO skid, connection for CIP system, leakage test for any connection, adjusting for flowrate and normalization data to be provided strictly , ensure the product water should be tested to ensure the results matching with the regulation, DoH and DOW standard, with all the work requirement for completing the work under the instructions of the site engineer.
2.1 | مضخة الضغط الواطئ المواصفات مدرجة في فقرة 2.1 | Filter Feed Pump See Specification 2.1 | Nos | 1
2.2 | مضخات حقن المواد الكيميائية المواصفات مدرجة في فقرة 2.2 | BIO FILMS INHIBITOR DOSING SYSTEM See Specification 2.2 | Nos | 1
2.3 | الفلاتر الرملية والكاربونية المواصفات مدرجة في فقرة 2.3 | MULTIMEDIA SAND FILTER & ACTIVATED CARBON FILTER | Nos | 2
2.4 | الفلاتر فائقة الترشيح السليلوزية المواصفات مدرجة في فقرة 2.4 | MICRON FILTRATION UNIT - 5 & 1 MICRON See Specification 2.4 | Nos | 2
2.5 | مضخات حقن مانع التكلس المواصفات مدرجة في فقرة 2.5 | ANTI-SCALANT DOSING SYSTEM See Specification 2.5 | Nos | 1
2.6 | مضخة الضغط العالي المواصفات مدرجة في فقرة 2.6 | HIGH PRESSURE PUMP See Specification 2.6 | Nos | 1
2.7 | الممبرينات المواصفات مدرجة في فقرة 2.7 | MEMBRANES See Specification 2.7 | Nos | 4
2.8 | الهاوزنك ممبرين المواصفات مدرجة في فقرة 2.8 | PRESSURE VESSELS See Specification 2.8 | Nos | 2
2.9 | منظومة اليوفي المواصفات مدرجة في فقرة 2.9 | UV-SYSTEM See Specification 2.9 | Nos | 1
2.1 | انابيب الخاصة بالمحطة وبين الخزانات وبين نقاط التوزيع المواصفات مدرجة في فقرة 2.10 | PIPING System See Specification 2.10 | LS | 1
2.11 | معدات السيطرة المواصفات مدرجة في فقرة 2.11 | INSTRUMENT LIST See Specification 2.11 | LS | 1
2.12 | خزان الغسيل الكيميائي المواصفات مدرجة في فقرة 2.12 | RO CIP TANK See Specification 2.12 | Nos | 1
2.13 | مضخة الغسيل الكيميائي المواصفات مدرجة في فقرة 2.13 | CIP PUMP See Specification 2.13 | Nos | 1
2.14 | مضخات الحقن للكلور المواصفات مدرجة في فقرة 2.14 | CHlORINE DOSING SYSTEM See Specification 2.14 | Nos | 1
2.15 | مضخة التجهيز المواصفات مدرجة في فقرة 2.15 | Delivery Pump See Specification 2.15 | Nos | 1
2.16 | البورد الخاص بالمحطة المواصفات مدرجة في فقرة 2.16 | CONTROL PANEL See Sepcification 2.16 | LS | 1
3 | تجهيز الفلانر الخاصة للمحطة وعدة الصيانة | Tool Kit & Consumable Materials
3.1 | الفلتر السليلوزي 5 مايكرون المواصفات مدرجة في فقرة 3.1 | Micron Filter Rating 5, Length 40“ See Specification 3.1 | Nos | 150
3.2 | الفلتر السليلوزي 1 مايكرون المواصفات مدرجة في فقرة 3.2 | Micron Filter Rating 1, Length 40“ See Specification 3.2 | Nos | 50
3.3 | تجهيز عدة الصيانة للمحطة المواصفات مدرجة في فقرة 3.3 | Tool Kit box See Specification 3.3 | LS | 1
4 | اعمال طلاء االارضيات للكرفانات | Floor Coating for Caravans
4.1 | طلاء الايبوكسي لغرفة الانفيرتر والطاقة الشمسية المواصفات مدرجة في فقرة 4.1 | Coating with Epoxy material (Jotun-Marathon 550 ) for RO Unit & Solar Invertor Carvans See Specification 4.1 | LS | 1
5 | التدريبات والوثائق الداعمة | Training & Manuals & Labelling Process
5.1 | اجراء تدريب للمشغلين المواصفات مدرجة في فقرة 5.1 | Conduct a Training for IRCS Staff See Specification 5.1 | LS | 1
5.2 | توفير كتلوك خاص للتشغيل والصيانة المواصفات مدرجة في فقرة 5.2 | Provision for O&M and Troubleshooting Manuals See Specification 5.2 | LS | 1
5.3 | ترقيم المعدات الكهربائية والميكانية الموجودة المواصفات مدرجة في فقرة 5.3 | Labeling Process for all the components See Specification 5.3 | LS | 1
5.4 | تقديم مخطط خاص بمحطة التحلية والانابيب والمعدات الكهربائية المواصفات مدرجة في فقرة 5.4 | As-built drawings See Specification 5.4 | LS | 1
6 | تفكيك ونقل المحطة القديمة | Dismantling & Mobilization for Exisiting RO Unit
6.1 | تفكيك ونقل المحطة القديمة المواصفات مدرجة في فقرة 6.1 | Dismantling & Mobilization for exisiting RO Unit See Specification 6.1 | LS | 1
|  | Total cost |  |  |  |  | 0
|  | Duration | n° of calendar days

## Technical Specifications
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
RO UNIT - 4 M3/hr / TDS UP TO 3,000 PPM ,
Supply and Installation for Reverse Osmosis Plant with production capacity of 4 M3/hr تجهيز ونصب محطة تحلية مياه بطاقة انتاجية 4 متر مكعب بالساعة تعمل على املاح لغاية 3,000
Babel Governorate /Al-Musayab District /Abu Jassim Village محافظة بابل/ قضاء المسيب / قرية أبو جاسم
Item |  | Description
1 | اعمال ربط مصدر الماء الخام | Connection to Water Source
1.1 | مضخة خاصة بالبئر السطحي | Complete Low Pressure Pump set comprised of pump(s), motor(s), suction, and discharge header, suction, and discharge isolating and NRV valves SS 304, pressure gauges and accessories as described Below: Manufacturer: European Brand ( Grundfoss with JP 6 A-A-CVBP or Equivalent ) Type: self-priming, single-stage centrifugal pumps Maximum Flow Rate: 5 m³/h Maximum Head: 57 meters Suction Lift Capability: 8-10 meters Quantity :1 No. Material of construction: SS304 Impeller:Stainless Steel (AISI 304) Power Consumption: 1.4 kW Voltage Options: 380 Volts Insulation Class: F Thermal overload protection equppied with Foot Valve + Filter Screen Suction Pipe (1.5") length around 8.5 meter with accessoriess The work including cleaning the area around the water sources, using concrete base fit with the size of pump and steel protection box with height of 1 meter for the pump and also for the well with gate to ensure proper maintaneance , the pump include also remote button for turining on/off the pump via control box close to the pump The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
1.1 | المضخة الخاصة بتجهيز المياه عن طريق الاسالة واعمال الربط بالاسالة | Complete Low Pressure Pump set comprised of pump(s), motor(s), suction, and discharge header, suction, and discharge isolating valves SS 304, pressure gauges and accessories as described Below: Manufacturer: European Brand ( Grundfoss CRN 10-4 or Equivalent ) Type: Vertical Centrifugal Flow: 7 m³/h Head 3 bar Quantity :1 No. Material of construction: SS316 Base: AISI 316 Impeller: Stainless steel Impeller: AISI 316 Material code: A Code for rubber: E Bearing: SIC MOTOR: Power 1.5 kW Phase/Voltage/Frequency/Operating: 380V/ 50 Hz / 3 Ph/ VFD The work includes connecting the RO unit to the existing water distribution network located approximately 30 meters away from the installation site. The connection shall be executed using a 2-inch HDPE or uPVC pipeline, complete with all necessary fittings, including suitable clamps and a shut-off valve. The works shall also include trench excavation, proper bedding, pipe laying, jointing, valve installation, and backfilling, ensuring full reinstatement of the area and compliance. The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
1.2 |  | Extend for the Pipline & Electrical Conduit from water source to the Raw water Tank Delivery Pipeline Setup: Total Length: Approximately 50 meters Street Crossing Segment: Approximately 8 meters (under road surface) Pipe Type: HDPE or uPVC pressure-rated pipe Diameter: 1.25" to 1.5" (DN32 to DN40), PN16 Crossing Protection: A 2" HDPE or PVC duct will be used to protect the pipeline across the street The ducted section will be buried at a depth of 80–100 cm Bedding will include sand for cushioning and a warning tape will be placed above the pipe for safety and future identification and all the sealing work to complete it perfectly
Electrical Cable and Power Supply: Cable Length: Approximately 50 meters Power Supply Type: 230V (Single-phase) Cable Specification: Single-phase: 3 x 4 mm² Cu cable , jordinian or Saudi Brand Conduit Protection: Cable will be routed through a 1.5" PVC or HDPE conduit Conduit will follow the same route as the water pipeline or be laid in a dedicated trench Burial depth of 80–100 cm with sand bedding and warning tape for safety
2 | تجهيز ونصب محطة التحلية سعة 2 متر مكعب بالساعة | Supply and Installation for Reverse Osmosis Plant with production capacity of 2 M3/hr :
Reverse Osmosis Treatment Plant 4 m3/hr TDS up to 2,000 ppm
Characteristic: Result Feed Flow Rate: 4 m3/hour Nos. of HBRO Skid: 1 No and Stainless-Steel Skid resistant to salinity (Sections sizes and material specification must be submitted in advance for review and approval to the ICRC-IRCS Engineers Design Feed: TDS 800-1,500 ppm at 25 °C Specific Gravity: 1.03 Feed Water: two available sources ( shallow water well & municipality water network ) pH value: @ 40°C 6.5 – 7.5 Turbidity: < 5 NTU SDI: Less than 5 Iron: Nil Temperature: 25 °C
2.1 | مضخة الضغط الواطئ | Complete Low Pressure Pump set comprised of pump(s), motor(s), suction, and discharge header, suction, and discharge isolating valves SS 304, pressure gauges and accessories as described Below: Manufacturer: European Brand ( Grundfoss CRN 10-4 or Equivalent) Type: Vertical Centrifugal Flow: 7 m3/hour Head: 4 bar Quantity :1 No. Material of construction: SS316 Base: EN 1.4408 Base: AISI 316 Impeller: Stainless steel Impeller: EN 1.4401 Impeller: AISI 316 Material code: A Code for rubber: E Bearing: SIC MOTOR: Power 2.2 KW Phase/Voltage/Frequency/Operating: 400V/ 50 Hz / 3 Ph/ VFD The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.2 | مضخات حقن المواد الكيميائية | Complete dosing station(s) comprised of pump(s), tank, and suction line with integrated foot valve, overflow valve, check valves, and accessories as described below Dosing Type: Inline Dosing Chemical: Genesys 80 (ENGLAND) or SMBS Flow rate :4 LPH @ 5.0 bar Type: Positive Displacement Diaphragm Type Manufacturer: Grundfos,PULSAFEDER (USA) or Equivalent Quantity: 1 No. Voltage/Phase/Frequency: 230V/ 50 Hz / 1 Ph TANK SET: Type: Cylindrical Storage Tank Quantity :1 No. Material: PE Volume :80 liters The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.3 | الفلاتر الرملية والكاربونية | Manufacturer: AQUATROL (TAIWAN) Flow :7m3/hr. Model VERTICAL Type :30”X72” Operating Pressure: 10 bar Maximum operating pressure: 10 bar Operating / Design temperature Ambient / 60 °C Maximum Quantity: 2 Nos. Material of Construction: FRP Mode of Operation: Manual valves Accessories Pressure gauges, sampling Interconnecting: UPVC piping etc. Certified to NSF/ANSI Standard 61 for material requirement only Interconnecting: UPVC piping etc. Granular Media Filter Max -Min Graduation size ( 9.5 - 0.4 mm) and as follow : 1. (9.5-6.5 mm ) at depth 10 cm 2. ( 6.5 - 2.5 mm ) at depth 10 cm 3. ( 2- 1 mm ) at depth 10 cm 4. ( 1-0.65 mm) at depth 10 cm 5. ( 0.4 mm ) at depth 20 cm Activated Carbon Media Filter: Employing a 75cm Depth, with Exclusion of media filter No. 4 and 5 Iodine number, mg/g : 1000 min Ash wt % : 4.0 (max) Moisture (As Packaged ), wt % : 5 (max) Density ( Apparent ), g /cc : 0.48 (min) Hardness Number : 95 (min) 12 US Mesh ( 1.70 mm) , 5 (max) < 40 US Mesh ( 0.425) , wt % : 4 ( max) The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.4 | الفلاتر فائقة الترشيح السليلوزية | Flow rate :10 m3/hr. per filter Manufacturer: (China or Taiwan) Quantity :2 Nos. Micron Rating / Length :5 Micron / 40 “+ 1 Micron / 40 “ Material of Construction: SS316 Type: Wound cartridge open end wash Nos. of Cartridge element / Housing: 7 Nos. Each The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.5 | مضخات حقن مانع التكلس | Complete dosing station(s) comprised of pump(s), tank, and suction line with integrated footvalve, overflow valve, check valves, and accessories as described below Dosing Type: Inline Dosing Chemical: AntiScalant or Genesys MP Flow rate :4 LPH @ 5.0 bar Type: Positive Displacement Diaphragm Type Manufacturer: Grundfos,PULSAFEDER (USA) or Equivalent Quantity: 1 No. Voltage/Phase/Frequency: 230V/ 50 Hz / 1 Ph TANK SET: Type: Cylindrical Storage Tank Quantity :1 No. Material: PE Volume :80 liters Accessories: Injection valve, Suction & Delivery Hose The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.6 | مضخة الضغط العالي | Complete high-pressure pump set comprised of pump(s), motor(s), suction, and discharge header, suction, and discharge isolating valves SS 304, check valves pressure gauges and accessories as described Below: Manufacturer: European Brand (Grundfoss CRN 10-14 or Equivalent) Pump: Model Vertical Multistage Pump Flow :7 m3/hr. Discharge Pressure :14 bar Quantity :1 No. Material of construction: Base: Stainless steel Base: AISI 316 Impeller: Stainless steel Impeller: AISI 316 Material code: A Code for rubber: E Bearing: SIC Accessories: Associated pipe wok, MOTOR Power: 5.5 KW Voltage/Phase/Frequency: 400V / 3 Ph / 50 Hz Mode of Operation: Through VFD Starter The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.7 | الممبرينات | Type: Spiral Wound Manufacturer: FILMTEC (USA) Model: BW30440i Material: Thin Film Composite Quantity : 4 Nos. The membrane configuration projection should be prepared in advance using ROSA software to ensure alignment with the Total Dissolved Solids (TDS) for both the Feed water and Product water, as well as the recovery requirement. Additionally, various scenarios should be outlined based on the forecasted feed water quality test results. The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.8 | الهاوزنك ممبرين | Type: H – Type series Manufacturer: BEL VESSELS (SPAIN) Model: 8"- 2 Elements Pressure rating :450 psi Material: FRP Diameter :8” Quantity :1 No.
2.9 | منظومة اليوفي | Manufacturer: (TAIWAN) Type of Lamps :35 Watts PHILIPS or Vieola Flow :4-5 m3/hr Head :2.0 bar Quantity :1 No. Material of construction: SS304 Lamp life: 9000 Hours Fitted with digital hour counter Power supply: 230 VAC 50 Hz The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.1 | انابيب الخاصة بالمحطة وبين الخزانات وبين نقاط التوزيع | All Low-Pressure Piping system shall be of UPVC From Raw water to Feed Pump of RO Units - ( Diameter of 2 inch ) From RO Units to the tanks and all the connections required From Treated tanks to the distribution points with the required Taps ( 4 taps SS304 ) - ( Diameter of 1.5 inch for the main header and with 1 inch for Taps ) Class E Nominal Pressure : 16 bar Velocity : 1.5 to 2 m/s and the pipes should be ranged between (1 1/2 ") and for Backwash ( 2 inch ) Evaluated and certified for conformance with DIN 8061 & 8062 (SASO 14-15/1998). Valve to be included on the on the LP Piping System side UPVC Ball Valves DN32 UPVC Check Valves DN32 UPVC Gate Valve DN32 UPVC Air Release Valve DN 20 All the Piping System should be installed using lined pipe clamps with the following features Material: Steel Finish: Electro Zinc Plated Lining: EPDM Rubber – working temperature -40 to +110°C Threads: M8/M10 welded boss Loads: Safe static tensile loads with limited deflection 0.7 to 1.2 KN
All High-Pressure Piping shall be of Stainless Steel, Material: SS304 Sehedule 40 Nominal Pressure : 150 bar Velocity : 2.5 to 3-5 m/s and the pipes should be ranged between ( 1 1/2 " ) Valve to be included on the on the HP Piping System side AISI 316 Regulating valves PN50 bar AISI 316 Check valves AISI Ball valves DN 15 (sampling valves) locations to be shared during the implementation All the Piping System should be installed using lined pipe clamps with the following features Material Size: A4 (1.4401; 316) Stainless Steel Threads: M8/M10 welded boss Lining: EPDM Rubber – working temperature -40 to +110°c Load: Safe static tensile loads All the piping System components size, specification, material, should be submitted in advance for review and approval by ICRC-IRCS Engineers before the installation phase
2.11 | معدات السيطرة | Pressure Gauge Pressure range: 0-4 bar (Qty:12) Pressure range: 0-40 bar (Qty:2) Type: Bourdon tube and glycerin filled Diameter: NS100 Ambient permissble temperature -20 to 40°C Water permissible temperature: 100°C Connection: 1/2" NPT Brand : Wika or Equivalent Inline Flow meters For Product, Reject Qty : 2 Type: PVC Rotameter flow meter Mount: Panel Rotor: PVDF Rotor pin: Titanium or stainless steel Water meter : Qty : 3 Material : plastic water meter complies with NSF / ANSI 61 Pressure range : up to 150 psi , Temperature All Parts in Contact with water are constructed of corrosion-resistant materials Body : FRP / Internals : Engineered thermoplastic Normal Flow : 1 -22 m3/hr The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
TDS meter Qty : 2 ( Feed and Product Water ) mounting: Panel Back. Reading Range: 0-5000 Automatic Temp compensation: from 0 - 100°C Automatic Float switch - 2 Nos. Low and High Pressure Switch Lower pressure switch : 0-2.5 bar High Pressure switch : 0-40 bar Brand :Danfass Brand Connection: 1/2" NPT
2.12 | خزان الغسيل الكيميائي | Type Cylindrical vertical tank Capacity / Volume 500 Liter Quantity 1 No. Material: High Density Linear Polyethelene, Accessories Associated piping, valves, floats, etc
2.13 | مضخة الغسيل الكيميائي | Complete CIP Pump set comprised of pump(s), motor(s), suction, and discharge header, suction, and discharge isolating valves SS 304, pressure gauges, check valves and accessories as described Below: Manufacturer: European Brand Pump Model / Type: Horizontal Centrifugal Flow :7 m3/h Head :3 bar Quantity :1 No. Material of construction: Base: Stainless steel Base: EN 1.4408 Base: AISI 316 Impeller: Stainless steel Impeller: EN 1.4401 Impeller: AISI 316 Material code: A Code for rubber: E Bearing: SIC Motor Power: 2.2 kW Phase / Voltage / Frequency / Operating: 400V/ 50 Hz / 3 Ph/ DoL The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.14 | مضخات الحقن للكلور | Complete dosing station(s) comprised of pump(s), tank, and suction line with integrated footvalve, overflow valve, check valves, and accessories as described below Dosing Type: Inline Dosing Chemical: Sodium Hypochlorite Flow rate :4 LPH @ 5.0 bar Type: Positive Displacement Diaphragm Type Manufacturer : Grundfos,PULSAFEDER (USA) or Equivalent Quantity: 1 No. Voltage/Phase/Frequency: 230V/ 50 Hz / 1 Ph The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation TANK SET: Type: Cylindrical Storage Tank Quantity :1 No. Material: PE : Volume :80 liters Accessories: Injection valve, Suction & Delivery Hose
2.15 | مضخة التجهيز | Complete Delivery Pump set comprised of pump(s), motor(s), suction, and discharge header, suction, and discharge isolating valves SS 304, pressure gauges and accessories as described Below: Manufacturer: European Brand Pump Model / Type: Horizontal Centrifugal Flow :3 m3/h Head :3 bar Quantity :1 No. Material of construction: Stainless Steel 304 Motor Power: 0.75 kW Phase / Voltage / Frequency / Operating: 400V/ 50 Hz / 3 Ph/ DoL The datasheet and Certificate of Origin should be provided in advance for ICRC-IRCS Engineers for review and validation
2.16 | البورد الخاص بالمحطة | Supply , Install , connect and operate (Main Control Panel - MCP ) Electrical Steel panel with diemensions ( 180 H x 60 W x 60 D ) cm ( Turkish Brand or equivalent ) , Mecano type , it contains bellow devices and components : 1. Change Over Switch (1-0-2 ) , Manual , 4 poles , SOCOMEC or equivalent , 100A . 2. MCCB (Molded Case Circuit Breaker ) ( 63-80 ) A , adjustable , 4 poles , Schneider Electric. .. QTY :01 (Main ) 3. MCB (Miniature Circuit Breaker ), 3 poles , 16A (8 nos. ) - for : a. S.P (Submersible Pump ) , b. D.P ( Delivery Pump ) , c. CL.P (Chlorine Dosing Pump ) , d. A.S.P (Anti-Scalant Dosing Pump ) , e. M.P ( Memberane Chleaning Dosing Pump ) , f. External Lighting . , g. Internal Lighting ., h. AC Split Unit 12000 BTU , i. Stand- by . 4. MCB , 3 poles , 32A, ( QTY :1. ) ,(H .P.P - High Preasure Pump ) 5. MCB , 3 poles , 25 A , ( 2 nos.) , for D.B (6 lines ) 6. VFD (Variable Frequency Drive ) : Schneider Electric , 3 ph , 380 vac - 416 VAC, smooth wave , all protection parameters , ( 3nos) , as bellow : -VFD 5.5 KW - High Presure Pump .- Schneider Electric -(1nos) -VFD 2.2 KW - Low Pressure Pump Pump .- Schneider Electric -(1 nos) -VFD 1.1 KW - Raw Water Pump .- Schneider Electric - ( 1nos) 7.Line Contactor 7.5 KW (QTY :1) : for High Pressure Pump.......................... before VFD. 8.Line Contactor 4 KW (QTY 2 ) : for ( Low Pressure Pump and Raw Water Pump ) .......before VFDs .
9.Contactors 4 KW , 25A , ( 6 nos ) for : Raw Water Pump(Shallow-well) , CLP(Cleaning Pump ) , Delivery Pump , Chlorinr Dosing Pump , Anti-Scalant Dosing Pump and Membarine Dosing Pump. 10.Over Loads : ( 2-4 ) A , 3 nos -- Delivery Pump , CLP and Submersible Pump . 11.Over Loads : ( 1.6 - 2.5 )A , ( 3nos ) - Chlorine Dosing Pump , Anti - Scalant and Membarine dosing Pump. Control Devices (contators , relays , timers , phase failures , MCBs , multi meter , connectors ,Emergency push-botton , selector switches , ventilation fans ) all other accessories (bus-bars , pvc trunks , cable ties , etc ,... ) Notes : 1. Certificate of origin for (power & control devices ( Schneider Electric ) should be provided to ICRC-IRCS Engineers . 2.The priority control operation for 1st (NG) ,2nd ( PV ) 3.Power and Control Diagrams as in attached drawings. 4. The work should be conform to : a. IEC 60364-4-41 Electrical installations of buildings - Protection for safety - Protection against electric shock. b.IEC 60364-4-42 Electrical installations of buildings - Protection for safety - Protection against thermal effects. 5. (Jordanian, Saudi or equivalent) cables in systematic way in apparent way by using Galvanized Steel Cable Tray inside and outside RO Unit in different sizes with accessories (elbo , joints , angles , etc... ) plus( bus-bars, pvc trunks, cable ties , etc ,... )with all basic connection requirements to achieve the work perfectly. see attached Drawings.
3 |  | Consumable Materials
3.1 | الفلتر السليلوزي 5 مايكرون | China or India ( SED CART, Silver Filteration) Material data sheet should be submitted
3.2 | الفلتر السليلوزي 1 مايكرون | China or India ( SED CART, Silver Filteration) Material data sheet should be submitted
3.3 | تجهيز عدة الصيانة للمحطة | Provision for the Sturdy Aluminum toolbox to store and transport the following toolkit items safely : Adjustable Wrench Pipe Wrench. Screwdriver Set (Flathead and Phillips) Adjustable Pliers Crescent (Adjustable) Pliers:Pipe Cutter Pipe Thread Tape (Teflon Tape): Pipe Sealant (Thread Sealant): Teflon Rope: Pipe Joint Compound: Pipe Clamps: Crimping Tool: Multimeter: For measuring voltage, current, and resistance in electrical circuits. Insulation Tape Wire Strippers Cable Ties (Zip Ties) Flashlight: Utility Knife Safety Glasses Work Gloves
4 |  | Floor Coating for Caravans
4.1 | الفلتر السليلوزي 5 مايكرون | The work includes surface preparation and epoxy coating of the metal floor inside two caravans (6×3 m and 3×3 m) designated for RO unit and solar inverter installation. Given the exposure to saline water and chemical handling, the coating system shall consist of one coat of Jotun Jotamastic Smart Pack primer followed by two coats of Jotun Marathon 550 epoxy. The total dry film thickness shall be approximately 1000 microns. Surface preparation shall include degreasing and mechanical cleaning or blasting to achieve proper adhesion. All coating works shall be carried out by experienced personnel using brush or roller, ensuring uniform coverage and compliance with manufacturer specifications.
5 |  | Training & Manuals & Labelling Process
5.1 | اجراء تدريب للمشغلين | Theoretical Understanding: Provide an overview of the principles of reverse osmosis and how the RO unit operates to desalinate water by removing salts and impurities. Explain the impact of salinity on the RO process and the unit's ability to effectively treat water with varying levels of salinity, up to 2,000 PPM. Operational Training:Conduct hands-on demonstrations of operating the RO unit at different salinity levels, adjusting parameters such as feed water flow rate, pressure, and recovery rate to optimize performance. Train IRCS staff on monitoring key operational parameters, including feed water quality, permeate flow rate, reject flow rate, and system recovery rate, and how to interpret these metrics to ensure proper functioning of the unit. Troubleshooting and Fault Identification: Provide detailed instruction on common issues and faults that may arise during RO unit operation, such as membrane fouling, scaling, pressure drop, and permeate quality deviations. Train staff on how to conduct systematic troubleshooting procedures to diagnose and address these issues, including visual inspections, pressure testing, membrane cleaning, and chemical dosing adjustments. Emphasize the importance of maintaining accurate records of operational data, maintenance activities, cleaning Process for the membrane by CIP System, and any deviations from normal operating conditions for troubleshooting purposes.
5.2 | توفير كتلوك خاص للتشغيل والصيانة | To facilitate efficient operation, maintenance, and troubleshooting of the mobile Reverse Osmosis (RO) unit, the contractor must adhere to the following guidelines when preparing O&M and Troubleshooting Manuals: Comprehensive Documentation: Provide comprehensive O&M manuals in Arabic languages that detail operational procedures, maintenance schedules, and troubleshooting protocols for the mobile RO unit, ensuring clarity and accessibility for operators and maintenance personnel. Clear Instructions: Include clear, step-by-step instructions for starting up, operating, shutting down, and cleaning the RO unit, as well as routine maintenance tasks such as filter replacement, membrane cleaning, and chemical dosing procedures. Safety Guidelines: Incorporate safety guidelines and precautions to be followed during operation, maintenance, and troubleshooting activities, emphasizing proper handling of chemicals, electrical equipment, and high-pressure components to ensure personnel safety. Component Descriptions: Describe each component of the mobile RO unit in detail, including its function, location, operating parameters, and maintenance requirements, to facilitate effective troubleshooting and replacement when necessary. Spare Parts List: Provide a comprehensive list of recommended spare parts, consumables, and tools required for routine maintenance and emergency repairs, along with guidance on inventory management and procurement procedures. Troubleshooting Flowcharts: Include troubleshooting flowcharts or decision trees to guide operators and maintenance personnel in diagnosing and resolving common issues and malfunctions encountered during operation, minimizing downtime and maximizing system uptime, Emergency Procedures: Outline emergency shutdown procedures, response protocols for system failures or malfunctions, and contact information for technical support and emergency services to ensure prompt and effective resolution of critical situations. Regular Updates: Commit to regularly updating the O&M and Troubleshooting Manuals reflect any modifications, upgrades, or improvements made to the mobile RO unit over time, ensuring that documentation remains current and relevant throughout its operational lifecycle.
5.3 | ترقيم المعدات الكهربائية والميكانية الموجودة | the contractor is required to implement a comprehensive labeling process for all components, electrical systems, piping, and chemical systems. This labeling ensures clarity, safety, and ease of operation and maintenance. The following guidelines should be adhered to: Component Labeling: Each component of the RO unit, including pumps, vessels, membranes, valves, instrumentation devices, and control panels, should be clearly labeled with descriptive tags or labels. Labels should include the component name, model number, serial number (if applicable), and any relevant specifications or operating parameters. Labels should be positioned prominently and securely affixed to the respective components to ensure easy identification and accessibility. Electrical System Labeling: All electrical components, including panels, breakers, switches, contactors, relays, and terminals, should be labeled according to their function and circuit designation. Labels should indicate the circuit name or number, voltage rating, current rating, phase designation (if applicable), and any safety warnings or instructions. Labels should be placed near the corresponding electrical equipment in a visible location and protected from damage or tampering. Piping Labeling:Piping systems associated with the RO unit, such as feed water lines, permeate lines, reject lines, concentrate recirculation lines, and chemical dosing lines, should be labeled at regular intervals. Labels should indicate the pipe contents, flow direction, operating pressure, and any relevant safety or hazard information. Labels should be positioned at strategic locations along the piping route, including near valves, junctions, and equipment connections, to facilitate maintenance and troubleshooting.
5.4 | تقديم مخطط خاص بمحطة التحلية والانابيب والمعدات الكهربائية | Accurate Representation: Provide As-Built drawings that accurately depict the final, constructed condition of the RO unit, reflecting any modifications, adjustments, or additions made during the construction process. to be placed inside the RO Unit Ro
6 | تفكيك ونقل المحطة القديمة | Dismantling & Mobilization for Exisiting RO Unit
6.1 | تفكيك ونقل وحدة التحلية الصغيرة إلى مخازن الهلال الأحمر العراقي في بابل | Provide all needed materials, labor, and equipment to dismantle the existing small-scale RO unit from its current location. This includes disconnecting the electricity, pipelines, tanks, sunshade, and fence. The unit including the tanks should then be transported to the IRCS warehouse in Babel Governorate (or another location assigned by the Babel IRCS Branch). The site must be cleaned and cleared of all debris and related materials after removal and completion of the project.